## Complete Map
Smart Meter Register Map with Float AC-Meter Model

Start	End	Size	R/W	Function codes	Name	Description	Type	Units	Scale Factor	Range of values
40001	40002	2	R	0x03	SID	Well-known value. Uniquely identifies this as a SunSpec Modbus Map	uint32			0x53756e53 ('SunS')

Start	End	Size	R/W	Function codes	Name	Description	Type	Units	Scale Factor	Range of values
40003	40003	1	R	0x03	ID	Well-known value. Uniquely identifies this as a sunspec model common (1)	uint16			1
40004	40004	1	R	0x03	L	Length of sunspec model common (1)	uint16	Registers		65
40005	40020	16	R	0x03	Mn	Smart Meter Manufacturer	string			e.g. "Fronius"
40021	40036	16	R	0x03	Md	Smart Meter Model	string			e.g. "Smart Meter 63A"
40037	40044	8	R	0x03	Opt	Smart Meter Name	string			e.g. "<primary>"
40045	40052	8	R	0x03	Vr	SW version of	string			e.g. "2.9"
40053	40068	16	R	0x03	SN	Smart Meter Serialnumber	string			e.g. "18370117"
40069	40069	1	R	0x03	DA	Modbus Device Address	uint16			1 - 247

Start	End	Size	R/W	Function codes	Name	Description	Type	Units	Scale Factor	Range of values
40070	40070	1	R	0x03	ID	Well-known value. Uniquely identifies this as a sunspec model ac_meter (21x)	uint16			211: Single Phase (AN or AB), 212: Split Single Phase (ABN), 213: WYE-Connect Three Phase (ABCN), 214: Delta-Connect Three Phase (ABC)
40071	40071	1	R	0x03	L	Length of sunspec model ac_meter (21x)	uint16	Registers		124
40072	40073	2	R	0x03	A	Total AC Current	float32	A
40074	40075	2	R	0x03	AphA	Phase A Current	float32	A
40076	40077	2	R	0x03	AphB	Phase B Current	float32	A		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40078	40079	2	R	0x03	AphC	Phase C Current	float32	A		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40080	40081	2	R	0x03	PhV	Line to Neutral AC Voltage (average of active phases)	float32	V
40082	40083	2	R	0x03	PhVphA	Phase Voltage AN	float32	V
40084	40085	2	R	0x03	PhVphB	Phase Voltage BN	float32	V		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40086	40087	2	R	0x03	PhVphC	Phase Voltage CN	float32	V		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40088	40089	2	R	0x03	PPV	Line to Line AC Voltage (average of active phases)	float32	V		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40090	40091	2	R	0x03	PPVphAB	Phase Voltage AB	float32	V		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40092	40093	2	R	0x03	PPVphBC	Phase Voltage BC	float32	V		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40094	40095	2	R	0x03	PPVphCA	Phase Voltage CA	float32	V		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40096	40097	2	R	0x03	Hz	Frequency	float32	Hz
40098	40099	2	R	0x03	W	Total Real Power	float32	W
40100	40101	2	R	0x03	WphA	Watts phase A	float32	W
40102	40103	2	R	0x03	WphB	Watts phase B	float32	W		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40104	40105	2	R	0x03	WphC	Watts phase C	float32	W		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40106	40107	2	R	0x03	VA	AC Apparent Power	float32	VA
40108	40109	2	R	0x03	VAphA	VA phase A	float32	VA
40110	40111	2	R	0x03	VAphB	VA phase B	float32	VA		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40112	40113	2	R	0x03	VAphC	VA phase C	float32	VA		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40114	40115	2	R	0x03	VAR	Reactive Power	float32	var
40116	40117	2	R	0x03	VARphA	VAR phase A	float32	var
40118	40119	2	R	0x03	VARphB	VAR phase B	float32	var		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40120	40121	2	R	0x03	VARphC	VAR phase C	float32	var		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40122	40123	2	R	0x03	PF	Power Factor	float32	PF
40124	40125	2	R	0x03	PFphA	PF phase A	float32	PF
40126	40127	2	R	0x03	PFphB	PF phase B	float32	PF		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40128	40129	2	R	0x03	PFphC	PF phase C	float32	PF		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40130	40131	2	R	0x03	TotWhExp	Total Real Energy Exported	float32	Wh
40132	40133	2	R	0x03	TotWhExpPhA	Total Watt-hours Exported phase A	float32	Wh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40134	40135	2	R	0x03	TotWhExpPhB	Total Watt-hours Exported phase B	float32	Wh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40136	40137	2	R	0x03	TotWhExpPhC	Total Watt-hours Exported phase C	float32	Wh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40138	40139	2	R	0x03	TotWhImp	Total Real Energy Imported	float32	Wh
40140	40141	2	R	0x03	TotWhImpPhA	Total Watt-hours Imported phase A	float32	Wh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40142	40143	2	R	0x03	TotWhImpPhB	Total Watt-hours Imported phase B	float32	Wh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40144	40145	2	R	0x03	TotWhImpPhC	Total Watt-hours Imported phase C	float32	Wh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40146	40147	2	R	0x03	TotVAhExp	Total Apparent Energy Exported	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40148	40149	2	R	0x03	TotVAhExpPhA	Total VA-hours Exported phase A	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40150	40151	2	R	0x03	TotVAhExpPhB	Total VA-hours Exported phase B	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40152	40153	2	R	0x03	TotVAhExpPhC	Total VA-hours Exported phase C	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40154	40155	2	R	0x03	TotVAhImp	Total Apparent Energy Imported	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40156	40157	2	R	0x03	TotVAhImpPhA	Total VA-hours Imported phase A	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40158	40159	2	R	0x03	TotVAhImpPhB	Total VA-hours Imported phase B	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40160	40161	2	R	0x03	TotVAhImpPhC	Total VA-hours Imported phase C	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40162	40163	2	R	0x03	TotVArhImpQ1	Total Reactive Energy Imported Quadrant 1	float32	varh		not supported
40164	40165	2	R	0x03	TotVArhImpQ1phA	Total VAr-hours Imported Q1 phase A	float32	varh		not supported
40166	40167	2	R	0x03	TotVArhImpQ1phB	Total VAr-hours Imported Q1 phase B	float32	varh		not supported
40168	40169	2	R	0x03	TotVArhImpQ1phC	Total VAr-hours Imported Q1 phase C	float32	varh		not supported
40170	40171	2	R	0x03	TotVArhImpQ2	Total Reactive Power Imported Quadrant 2	float32	varh		not supported
40172	40173	2	R	0x03	TotVArhImpQ2phA	Total VAr-hours Imported Q2 phase A	float32	varh		not supported
40174	40175	2	R	0x03	TotVArhImpQ2phB	Total VAr-hours Imported Q2 phase B	float32	varh		not supported
40176	40177	2	R	0x03	TotVArhImpQ2phC	Total VAr-hours Imported Q2 phase C	float32	varh		not supported
40178	40179	2	R	0x03	TotVArhExpQ3	Total Reactive Power Exported Quadrant 3	float32	varh		not supported
40180	40181	2	R	0x03	TotVArhExpQ3phA	Total VAr-hours Exported Q3 phase A	float32	varh		not supported
40182	40183	2	R	0x03	TotVArhExpQ3phB	Total VAr-hours Exported Q3 phase B	float32	varh		not supported
40184	40185	2	R	0x03	TotVArhExpQ3phC	Total VAr-hours Exported Q3 phase C	float32	varh		not supported
40186	40187	2	R	0x03	TotVArhExpQ4	Total Reactive Power Exported Quadrant 4	float32	varh		not supported
40188	40189	2	R	0x03	TotVArhExpQ4phA	Total VAr-hours Exported Q4 Imported phase A	float32	varh		not supported
40190	40191	2	R	0x03	TotVArhExpQ4phB	Total VAr-hours Exported Q4 Imported phase B	float32	varh		not supported
40192	40193	2	R	0x03	TotVArhExpQ4phC	Total VAr-hours Exported Q4 Imported phase C	float32	varh		not supported
40194	40195	2	R	0x03	Evt	Meter Event Flags	bitfield32			currently hardcoded to zero

Start	End	Size	R/W	Function codes	Name	Description	Type	Units	Scale Factor	Range of values
40196	40196	1	R	0x03	ID	Identifies this as End block	uint16			0xFFFF
40197	40197	1	R	0x03	L	Length of model block	uint16			0x0

## common (1)
Start	End	Size	R/W	Function / codes	Name	Description	Type	Units	Scale Factor	Range of values
1	1	1	R	0x03	ID	Well-known value. Uniquely identifies this as a sunspec model common (1)	uint16			1
2	2	1	R	0x03	L	Length of sunspec model common (1)	uint16	Registers		65
3	18	16	R	0x03	Mn	Smart Meter Manufacturer	string			e.g. "Fronius"
19	34	16	R	0x03	Md	Smart Meter Model	string			e.g. "Smart Meter 63A"
35	42	8	R	0x03	Opt	Smart Meter Name	string			e.g. "<primary>"
43	50	8	R	0x03	Vr	SW version of	string			e.g. "2.9"
51	66	16	R	0x03	SN	Smart Meter Serialnumber	string			e.g. "18370117"
67	67	1	R	0x03	DA	Modbus Device Address	uint16			1 - 247

## ac_meter (21x)
Start	End	Size	R/W	Function / codes	Name	Description	Type	Units	Scale Factor	Range of values
1	1	1	R	0x03	ID	Well-known value. Uniquely identifies this as a sunspec model ac_meter (21x)	uint16			211: Single Phase (AN or AB), 212: Split Single Phase (ABN), 213: WYE-Connect Three Phase (ABCN), 214: Delta-Connect Three Phase (ABC)
2	2	1	R	0x03	L	Length of sunspec model ac_meter (21x)	uint16	Registers		124
3	4	2	R	0x03	A	Total AC Current	float32	A
5	6	2	R	0x03	AphA	Phase A Current	float32	A
7	8	2	R	0x03	AphB	Phase B Current	float32	A		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
9	10	2	R	0x03	AphC	Phase C Current	float32	A		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
11	12	2	R	0x03	PhV	Line to Neutral AC Voltage (average of active phases)	float32	V
13	14	2	R	0x03	PhVphA	Phase Voltage AN	float32	V
15	16	2	R	0x03	PhVphB	Phase Voltage BN	float32	V		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
17	18	2	R	0x03	PhVphC	Phase Voltage CN	float32	V		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
19	20	2	R	0x03	PPV	Line to Line AC Voltage (average of active phases)	float32	V		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
21	22	2	R	0x03	PPVphAB	Phase Voltage AB	float32	V		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
23	24	2	R	0x03	PPVphBC	Phase Voltage BC	float32	V		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
25	26	2	R	0x03	PPVphCA	Phase Voltage CA	float32	V		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
27	28	2	R	0x03	Hz	Frequency	float32	Hz
29	30	2	R	0x03	W	Total Real Power	float32	W
31	32	2	R	0x03	WphA	Watts phase A	float32	W
33	34	2	R	0x03	WphB	Watts phase B	float32	W		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
35	36	2	R	0x03	WphC	Watts phase C	float32	W		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
37	38	2	R	0x03	VA	AC Apparent Power	float32	VA
39	40	2	R	0x03	VAphA	VA phase A	float32	VA
41	42	2	R	0x03	VAphB	VA phase B	float32	VA		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
43	44	2	R	0x03	VAphC	VA phase C	float32	VA		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
45	46	2	R	0x03	VAR	Reactive Power	float32	var
47	48	2	R	0x03	VARphA	VAR phase A	float32	var
49	50	2	R	0x03	VARphB	VAR phase B	float32	var		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
51	52	2	R	0x03	VARphC	VAR phase C	float32	var		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
53	54	2	R	0x03	PF	Power Factor	float32	PF
55	56	2	R	0x03	PFphA	PF phase A	float32	PF
57	58	2	R	0x03	PFphB	PF phase B	float32	PF		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
59	60	2	R	0x03	PFphC	PF phase C	float32	PF		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
61	62	2	R	0x03	TotWhExp	Total Real Energy Exported	float32	Wh
63	64	2	R	0x03	TotWhExpPhA	Total Watt-hours Exported phase A	float32	Wh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
65	66	2	R	0x03	TotWhExpPhB	Total Watt-hours Exported phase B	float32	Wh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
67	68	2	R	0x03	TotWhExpPhC	Total Watt-hours Exported phase C	float32	Wh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
69	70	2	R	0x03	TotWhImp	Total Real Energy Imported	float32	Wh
71	72	2	R	0x03	TotWhImpPhA	Total Watt-hours Imported phase A	float32	Wh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
73	74	2	R	0x03	TotWhImpPhB	Total Watt-hours Imported phase B	float32	Wh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
75	76	2	R	0x03	TotWhImpPhC	Total Watt-hours Imported phase C	float32	Wh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
77	78	2	R	0x03	TotVAhExp	Total Apparent Energy Exported	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
79	80	2	R	0x03	TotVAhExpPhA	Total VA-hours Exported phase A	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
81	82	2	R	0x03	TotVAhExpPhB	Total VA-hours Exported phase B	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
83	84	2	R	0x03	TotVAhExpPhC	Total VA-hours Exported phase C	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
85	86	2	R	0x03	TotVAhImp	Total Apparent Energy Imported	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
87	88	2	R	0x03	TotVAhImpPhA	Total VA-hours Imported phase A	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
89	90	2	R	0x03	TotVAhImpPhB	Total VA-hours Imported phase B	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
91	92	2	R	0x03	TotVAhImpPhC	Total VA-hours Imported phase C	float32	VAh		This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
93	94	2	R	0x03	TotVArhImpQ1	Total Reactive Energy Imported Quadrant 1	float32	varh		not supported
95	96	2	R	0x03	TotVArhImpQ1phA	Total VAr-hours Imported Q1 phase A	float32	varh		not supported
97	98	2	R	0x03	TotVArhImpQ1phB	Total VAr-hours Imported Q1 phase B	float32	varh		not supported
99	100	2	R	0x03	TotVArhImpQ1phC	Total VAr-hours Imported Q1 phase C	float32	varh		not supported
101	102	2	R	0x03	TotVArhImpQ2	Total Reactive Power Imported Quadrant 2	float32	varh		not supported
103	104	2	R	0x03	TotVArhImpQ2phA	Total VAr-hours Imported Q2 phase A	float32	varh		not supported
105	106	2	R	0x03	TotVArhImpQ2phB	Total VAr-hours Imported Q2 phase B	float32	varh		not supported
107	108	2	R	0x03	TotVArhImpQ2phC	Total VAr-hours Imported Q2 phase C	float32	varh		not supported
109	110	2	R	0x03	TotVArhExpQ3	Total Reactive Power Exported Quadrant 3	float32	varh		not supported
111	112	2	R	0x03	TotVArhExpQ3phA	Total VAr-hours Exported Q3 phase A	float32	varh		not supported
113	114	2	R	0x03	TotVArhExpQ3phB	Total VAr-hours Exported Q3 phase B	float32	varh		not supported
115	116	2	R	0x03	TotVArhExpQ3phC	Total VAr-hours Exported Q3 phase C	float32	varh		not supported
117	118	2	R	0x03	TotVArhExpQ4	Total Reactive Power Exported Quadrant 4	float32	varh		not supported
119	120	2	R	0x03	TotVArhExpQ4phA	Total VAr-hours Exported Q4 Imported phase A	float32	varh		not supported
121	122	2	R	0x03	TotVArhExpQ4phB	Total VAr-hours Exported Q4 Imported phase B	float32	varh		not supported
123	124	2	R	0x03	TotVArhExpQ4phC	Total VAr-hours Exported Q4 Imported phase C	float32	varh		not supported
125	126	2	R	0x03	Evt	Meter Event Flags	bitfield32			currently hardcoded to zero

## End Block
Start	End	Size	R/W	Function / codes	Name	Description	Type	Units	Scale Factor	Range of values
1	1	1	R	0x03	ID	Identifies this as End block	uint16			0xFFFF
2	2	1	R	0x03	L	Length of model block	uint16			0x0